## Slide 1
Rosemount 2230 Graphical Field Display

## Slide 2: System Overview
2240S Multi-Input Temperature Transmitter
5900S Radar Level Gauge
3051S Pressure Transmitter
2230 Graphical Field Display
2410 Tank Hub
Tankbus: FOUNDATIONTM fieldbus
Fieldbus

## Slide 3: 2230 Graphical Field Display
Presents inventory Tank gauging data from the hub
Language selection possibilities
  English, French, German, Spanish, Italian, and Portuguese
Custody Transfer View
  Displays Level & Avg temp for each tank
Up to 3 displays connected to one tank hub

## Slide 4: 2230 Graphical Field Display
4 panel buttons for easy navigation
Field configuration
  view and units
Data update time: 2s
Backlit LCD
Remote installation
  Pipe/wall installation kit (optional)

## Slide 5: Available Field Data
Viewable variables | 
Level | Vapor temperature
Ullage | Product temperature
Level rate | Tank average temperature
Signal strength | Temperature spot 1 to 16
Free water level | Observed density
Vapuor pressure | Reference density
Liquid pressure | Flow rate
Air pressure | Total Observed Volume
Ambient temperature | User defined 1 to 5

## Slide 6: 2230 Graphical Field Display
Tank name (up to 10 tanks)
”Live” indication
Four soft keys
Alarm /Error symbol
Large-sized digits, 25 mm (1 in.) in single value view

## Slide 7: Configuration via TankMaster

## Slide 8: 2230 Installation Considerations
Intrinsically safe
Mount on a plate towards a wall or similar
  Optional pipe/wall installation kit
Powered over the Tankbus from 2410
  Requires 30 mA
Daisy-chain connection possible
Built-in termination jumper
  To be connected if required
Configured in TankMaster

## Slide 9: Wiring
Tankbus
  X2 and X3 terminal
  Output for daisy-chain
Cable shield
  X1 terminal
Termination jumper
  X3 (-) output and X4
  Only if it is the last device on the Tankbus
X4: Tankbus terminator
X2: Tank Bus (+) input
X3: Tank Bus (-) input
X1:Cable Shield
Temination jumper
X2: Tank Bus (+) output
X3: Tank Bus (-) output
X1:Cable Shield
*Dual Terminals for Daisy chaining the field

## Slide 10: LEDs and Dip Switches
Dip Switch
  Write Protection
Transmit/ Receive LEDs
Status LED
Reset button

## Slide 11: Switches
Switches
  Simulates measurement values from tanks
  Write protect
    Protects all configuration in 2230
Reset button
  Restores configuration to factory settings
1
2
3
4
Number | Name | Description
1 | Simulate | Enables simulation of tank monitoring
2 | Write Protect | Enables write protection of configuration data
3 | Spare | Not used
4 | Spare | Not used
Notes: Ta reda på mer om hur simulation fungerar

## Slide 12: Configuration options
TankMaster
  Described in WinSetup presentation
Display softkeys
  Tree based menu
  Selectable options
    Variables
    Tanks
    Units
    Toggle Time
    Language
  Service Menu
    For display troubleshooting in field

## Slide 13: Service Menu
Status
  Current status for network and hardware
Custody Transfer View
  Displays Level & Avg temp for each tank
LCD Test
  Chequered pattern to test the whole display area
  Returns to normal mode when test is completed
Factory Settings
  Restore factory settings, all user configuration will be lost
Restart & About

## Slide 14: Display contrast
Increase contrast
  Press the two buttons on the right-hand side simultaneously
Decrease contrast
  Press the two buttons on the left-hand side simultaneously
Decrease contrast
Increase contrast

## Slide 15: Reset the 2230 to factory settings
Two ways to reset the 2230:
  Internal button
    Press to restore factory settings
  WinSetup
    Send reset command via field bus
    Holding register 65510
Reset button
Notes: Hur funkar default load... ??

## Slide 16: Troubleshooting
Symptoms | Actions
No communication with 2230 using FISCO | Faulty communication cabling – check cabling No fieldbus termination or too many terminations Make sure that the last devices in the FISCO fieldbus is terminated
No possible to change configuration | Make sure hardware write protection switch is off Remove software write protection using TankMaster Winsetup
NOTE! Firmware cannot be ugraded in field! |